## Sheet1
Automatic Sash Positioning System ASPS™
Air Consumption For Cylinders
CUSTOMER: | [5 empty] | New-Tech™
PO Box 1944
Midland, MI 48641-1944
PHONE: 866-631-8324
FAX: 989-631-8362
www.newtechtm.com
Note: substitute new figures in box
| BORE= |  | 1 | IN. | Standard Cylinder Dia.
| STROKE= |  | 18 | IN. | Sash travel (open or close)
| PRESSURE= |  | 20 | PSI | Normally 12 to 18 psi
| TIME= |  | 3 | SEC. | Sash Open or Closed Speed
| PRESSURE DROP= |  | 5 | PSI | Cylinder Resistance (break-away)
|  | AREA= | 0.785 | SQ. FT.
|  | VOLUME= | 14.13 | CU.IN.
|  | FORCE= | 15.7 | LBS
|  | CFM= | 0.16354 | CU. FT. MIN.
|  | SCFM= | 0.38605 | STD. CU. FT./MIN.
|  | CV= | 0.029958 | Usage Per Sash Cycle
Using large AIR tank 305 CU FT. = |  |  | 527040 | CU. IN.
|  |  | 37299.3631 | Strokes divided by 2 = Cycles (open and close)
|  |  | 18649.6815 | Total Sash Cycles ASPS™
Using 305 CU. FT. AIR tank